## Slide 1: Gasfitting certification
8 April 2014

## Slide 2: Gasfitting Certification
Amendments to certification of gasfitting and installation prescribed electrical work –
Came into effect in July 2013
Implement certification review
Address weaknesses in certification - eg non-application to < 15 kg installations
Extended to all gasfitting
Document quality of work and the safety and compliance of the product
Potential to integrate with business processes

## Slide 3: Why certification?
Certification influences compliance by providing:
Means to record and exchange information about the status of work, and the responsibility for safety
A check list to remind practitioners of the safety critical aspects of gasfitting, and
A visible, traceable path for investigations and audits of gasfitting and worker competency
A good regulatory intervention is one that increases the probability that the regulated activity will meet the expectations of society.

## Slide 4: risk management Approach
Good Regulatory Practice expects application of Risk Management principles to ensure that the level of regulatory intervention is proportional to risk – of (not) achieving safety compliance. So:
Low-risk gasfitting is self-certified
General and high-risk gasfitting require more rigorous verification
High-risk gasfitting requires public lodgement
Notes: Addresses the question: “Why have three confusing gasftitting categories – Low-risk, General and High-risk?”

## Slide 5: Deciding on gasfitting risk category
The key is to assess whether gasfitting is low-risk, or high-risk or general gasfitting – in that order:
Decide whether the gasfitting meets any of the low-risk criteria. If so, it is low-risk gasfitting.
If the gasfitting is not low-risk, decide whether it meets any of the high-risk criteria. If so, it is high-risk gasfitting.
If it is not low-risk or high-risk gasfitting, it is general gasfitting.

## Slide 6: Is it gasfitting?
Work that is not gasfitting does not need gasfitting certification – see section 5 of the PG&D Act.
Examples that are not gasfitting:
Work on any gas storage container
Work that only involves consumer-adjustable controls
Work upstream of point of supply
Some maintenance

## Slide 7: Low-risk gasfitting
Work defined as low-risk gasfitting is, in general, work that before 1 July 2013 did not require certification:
No longer a ‘less than 15 kg’ exemption

## Slide 8: Low-risk gasfitting
The replacement of a gas appliance with an equivalent gas appliance, provided—
  (i) the work does not involve a significant change; and
  (ii) the appliance is not located in a caravan or boat with sleeping quarters.
Gasfitting for the maintenance of fittings and appliances in an installation – other than repair work carried out following a notifiable accident.
  Replacement of instrumentation and related controls – provided the work doesn’t result in the repositioning or disturbance of other pipework.

## Slide 9: Low-risk gasfitting
Setting of safety devices, combustion conditions and controls that are not consumer (or refueller) adjustable.
Gasfitting in a gas engineering workshop, manufacturing facility, gas test facility, laboratory, hospital, research project, or teaching institution, but only if—
  the work is the installation of temporary pipework; and
  the fittings or appliances are used for experimental, testing, demonstration, teaching, or research purposes.

## Slide 10: High risk gasfitting
Work defined as high-risk gasfitting means that additional care is considered necessary to improve the probability of compliance:
Work is outside scope of means of compliance
Regulations apply installation standard outside its scope
Additional hazards exist – eg proximity to hazardous area

## Slide 11: High-risk gasfitting
Alteration of or addition to an existing installation
Work carried out in not accordance with the means of compliance in the Installation Standard
Work on an installation that includes gas pressure raising equipment
Repair work following a notifiable incident
Work on domestic premises where the maximum operating pressure is more than 7 kPa for NG or more than 14 kPa for LPG
Work in a building of more than three storeys which contains three or more separate dwellings

## Slide 12: High-risk gasfitting
Work done to AS/NZS 5601.1 but where the pressure supply to the installation is greater than 200 kPa
Work done to AS/NZS 5601.2 but where the pressure supply of the installation is greater than 3 kPa
Work done within 20 metres of a hazardous area
Work in a building in which air pressure is controlled by a mechanical ventilation system
Work where air for combustion is provided by mechanical means either at above or below atmospheric pressure
Work in a caravan or boat with sleeping accommodation

## Slide 13: General gasfitting
… everything else

## Slide 14: Examples
The following examples demonstrate how to work out the gasfitting risk category.

## Slide 15: Example 1 – New installation
If you install a storage water heater in a new installation that meets the means of compliance in the installation standard:
The work is not low-risk or high-risk so it is general gasfitting
The work requires a CoC as well as a GSC

## Slide 16: Example 2 - Replacement
If you replace a storage water heater with an equivalent that does not result in a charge to the installation pipework, gas type, gas pressure, energy consumption, ventilation or operation of the installation:
The work is low-risk gasfitting because it meets one of the low-risk criteria
The work requires a GSC
Note: This applies to any gasfitting involved in changing a part under warranty
Notes: This example encompasses the scenario of changing parts under warranty.

## Slide 17: Example 3 – modification
If you replace a storage water heater with another of the same energy consumption, no change to the flue, but a change in the position of the gas inlet connection on the heater from left hand to right hand:
The repositioning of the gas inlet connection makes the work general gasfitting – it is not low-risk and it is not high-risk
The work requires a CoC and a GSC

## Slide 18: Example 4 – other means of compliance
If you install a storage water heater in a new domestic installation that doesn’t meet the means of compliance in the installation standard:
There has to be a Certified Design if not using means of compliance in the Installation Standard
The work is not low-risk; it is high-risk because it meets one of the high-risk criteria
The work requires a CoC and a GSC, and details on the high-risk register

## Slide 19: Example 5 – Pipework only
If you install the pipework for the new installation of a storage water heater without connecting it to the gas supply, and someone else is going to install the appliances and connect the gas supply:
The pipework installation is not low-risk or high-risk so it is general gasfitting &
This work requires a CoC for the part installation
Other parts of the work also require a CoC
The installation will require a GSC when it is connected by the person who connects the gas supply, or when completed
The person doing the connection may rely on the CoC for the pipework

## Slide 20: Example 6 – Pipework and connection
If you install the pipework for the new installation of a storage water heater and connect it to the gas supply and someone else is going to install the appliances and connect the appliance:
The pipework installation is not low-risk or high-risk so it is general gasfitting
The work requires a CoC and GSC for the part installation
The installation of the appliance is not low-risk or high-risk, and requires a CoC and GSC when it is connected

## Slide 21: Example 7 – Repairs
The repair of damage to pipework is regarded as maintenance of fittings, unless it is repair work following a notifiable accident.
For example, brazing to repair damage done by a builder's nail driven into a copper pipe:
The work is low-risk gasfitting and a CoC is not required
The connected or completed gasfitting work requires a GSC.
Notes: Auckland MPGD asked another similar question:
Repairing either a leaking mechanical joint or a brazed joint in pipe work.
The repair of a leaking mechanical joint or a brazed joint in pipework can be regarded as maintenance of fittings. As such, unless it is repair work following a notifiable accident, it is low-risk gasfitting.
The connected or completed gasfitting requires a GSC.

## Slide 22: Responsibility – part installation
If you work on part of an installation, under GSMR 52B you, as certifier, have to be satisfied that:
  the part installation worked on is safe to use, and
  the work has not adversely affected any other part of the installation
For example, if you are replacing a gas heater and do a GSC, would you be expected to check if the cooker had say a safety chain on it etc?
In most cases, no – the obligation is to ensure the work has not adversely affected the rest of the installation
If your work involved the cooker or you happened to notice something – duty of care applies
What service did you offer?

## Slide 23: Supply pressure interpretation I
LPG point of supply begins at the bottle valve outlet. Most LPG installations have a section of pipe work operating at cylinder pressure, eg:
From the interface of the bottle valve outlet and the immediate POL bull nose single stage regulator fitting - a few mm
The flexible pigtail between the bottle valve and the change-over or first stage regulator
The pigtails and manifold for a bank of cylinders
Pigtails supply a manifold through to a first stage regulator with an outlet pressure of 70 kPa, a 50m section of pipe to a second stage regulator with an outlet pressure of less than 3 kPa and a final section of pipe to the appliances
Does the presence of any of these make the whole installation high-risk?

## Slide 24
In each example there is a section of pipework exposed to cylinder pressure:
Gasfitting involving a section of pipework exposed to cylinder pressure that is not low-risk gasfitting is high-risk gasfitting
Energy Safety considers that downstream of a point in an installation where gas is regulated to below 3 kPa (AS/NZS 5601.2) or 200 kPa (AS/NZS 5601.1), gasfitting on that part need not be considered high-risk simply because the pressure at the point of supply (as defined in the regulations) is above those limits.
Supply pressure interpretation II
Notes: Note: However, because regulation 5A(2)(b) (vi) & (vii) use the term ‘point of supply’ (which is defined in the regulations), these two high-risk criteria can be interpreted as applying to the whole of an installation where the pressure at the point of supply is greater than the 3 kPa (LPG) or 200 kPa (natural gas) limits.
Energy Safety will be proposing an amendment to the regulations to clarify this point.

## Slide 25: Example 8 – Replacement of pigtail
What about the replacement of a pigtail and integral POL bull nose bottle fitting?
The replacement of a pigtail and integral PoL bullnose fitting can be regarded as maintenance of fittings so, unless it is repair work following a notifiable accident, the work is low-risk gasfitting – regardless of supply pressure
The connected or completed gasfitting work requires a GSC

## Slide 26: Multiple contractors
Each gasfitter treats the work they do on its own merits. For example:
  A gasfitter completes work and classes that work correctly as general gasfitting.
  At the same time a second gasfitter completes and connects some high-risk gasfitting to the first gasfitter’s work.
  Does the first gasfitter have to re-categorise his work to high-risk as it now forms part of the second gasfitter’s?
No, not if the work is done independently
Each job should have a CoC for the work of each gasfitter, and the high risk work lodged on the high-risk database
The completed installation requires a GSC or GSCs
Notes: This kind of situation is one where careful documentation could be especially useful.

## Slide 27: Staged work
Each gasfitter treats the work they do on its own merits. For example:
  A gasfitter completes work and classes that work correctly as general gasfitting.
  Shortly afterwards, a second gasfitter completes and connects some general gasfitting to the first gasfitter’s work.
This is staged work on a new installation
The second gasfitter’s work is not high-risk gasfitting merely on the basis that the other work was completed first
The work of both gasfitters requires a CoC or CoCs that between them cover all the work
The completed installation requires a GSC or GSCs
Notes: This kind of situation is one where careful documentation could be especially useful.
If the first gasfitter anticipates the second gasfitter’s work, eg by putting in a transition fitting it would be clearer that the work is staged.
The original Auckland MPGD question assumed that the second gasfitter’s work in doing an extension was high-risk gasfitting and, on that assumption, asked whether that made the whole installation high-risk.
If the situation is that the first gasfitter has correctly categorised his work as general gasfitting and the second then does some work that does not change the classification of the first gasfitter’s work whether or not t is high-risk (eg by not following the means of compliance) . There is certainly is no need for further certification of the first gasfitter’s work.

## Slide 28: Example 9 – replacing fittings
What about the replacement of a combination gas valve, such as a Unitrol or SIT, bearing in mind they have consumer adjustable thermostats?
The replacement of a gas valve in an installed appliance is maintenance, provided it is not repair work following a notifiable accident, so the work is low-risk gasfitting
The connected or completed gasfitting work requires a GSC
Notes: The definition of gasfitting has an exclusion related to the adjustment (not replacement) of consumer-operated controls.
A similar question from Auckland MPGD was:
The replacement of a thermocouple on a water heater or deep fryer for example.
The replacement of a thermocouple on a water heater can be regarded as maintenance, so provided it is not repair work following a notifiable accident, the work is low-risk gasfitting.
Alternatively, assuming this example relates to the question of disturbance of pipework, the replacement of a thermocouple can be regarded as replacement of instrumentation or related controls so, provided the pipework not directly associated replaced equipment is not repositioned or disturbed, the work is low-risk gasfitting.
In either case, the connected or completed low-risk gasfitting work and requires a GSC.
Another similar question from Auckland MPGD was:
The replacement of a mechanical thermostat together with its associated probe and capillary on a deep fryer.
The replacement of a mechanical thermostat together with its associated probe and capillary on a deep fryer can be regarded as maintenance so, provided it is not repair work following a notifiable accident, the work is low-risk gasfitting.
Alternatively, assuming this example relates to the question of disturbance of pipework, provided the replacement of a mechanical thermostat together with its associated probe and capillary on a deep fryer does not disturb pipework other than the capillary, the work is low-risk gasfitting.
In either case, the connected or completed low-risk gasfitting work and requires a GSC.

## Slide 29: Example 10 – disturbance of pipework
Please define in more detail “disturbance of pipework”.
Disturbance of pipework in refers to disturbing or moving it from its original position in the course of carrying out the gasfitting work – GSMR 5A(1)(c)
NB this is one element of gasfitting that under the previous regulations was exempt from certification

## Slide 30: Overlapping high-risk criteria - I
There have been questions about an apparent conflict in high-risk criteria:
Work in domestic premises where the maximum operating pressure is more than 7 kPa for natural gas or more than 14 kPa for LPG – GSMR 5A(2)(b)(iv)
Work done to 5601.1 (natural gas) where the supply pressure to the installation is greater than 200 kPa – GSMR 5A(2)(b)(vii)
Work done to 5601.2 (LPG) where the supply pressure to the installation is greater than 3 kPa – GSMR 5A(2)(b)(vi)

## Slide 31: Overlapping high-risk criteria - II
These high-risk criteria apply to different situations. If one or more high-risk condition applies then, provided it is not low risk, the gasfitting is high-risk:
The operating pressure criteria of 7 kPa (natural gas) and 14 kPa (LPG) are benchmarks above which there are additional installation requirements:
  eg for domestic installations – clause 5.2 of AS/NZS 5601.1
  eg for gas appliance design – clause 2.3.1.14 of NZS/AS 3645.1
The scope of AS/NZS 5601.1 and AS/NZS 5601.2 limit the means of compliance to installations designed to operate with a gas supply pressure ≤ 200 kPa and 3 kPa respectively.
Notes:   clause 5.2 of AS/NZS 5601.1 - additional requirements include marking of pipework and overpressure protection
  clause 2.3.1.14 of NZS/AS 3645.1 - requirement for overpressure protection

## Slide 32: Everything is to be certified
Is there any gasfitting work that is categorised as exempt (or does not require the completion of a GSC)?
  In other words anything that fits within the definition of gasfitting in s5 of the PGD Act 2006 requires some sort of certification.
There is no gasfitting installation work that is exempt – all gasfitting requires at least the completion of a GSC
Notes: Note: The regulations are unclear whether gasfitting undertaken solely for the purposes of testing, eg pressure tests or testing under NZS 5255, is not installation work that should require certification. Energy Safety will be proposing an amendment to the regulations to clarify this point.
Such a change would not affect the status of changing a thermocouple and other similar maintenance work classified as low-risk gasfitting because this can have a material effect on the operation of an installation.

## Slide 33: Dates on certification forms
There are two boxes on the combined CoC & GSC form. One says ‘date gasfitting performed’ and the other next to it, says ‘enter the specific date or span of dates’. Is it necessary to have two references to dates?
The combined CoC-GSC published on Energy Safety’s website has two date boxes:
  ‘Date or dates on which the work was done’; and
  ‘Date of completion’
The first relates to the date on which the work was done and the second relates to the date the certification was completed – both are relevant

## Slide 34: Completion date for staged work
The combined CoC-GSC asks for the ‘date of gas connection’. How do I certify a job where the work is completed in stages and the gas is livened up to or turned on to each stage as they are completed?
The regulations allow for flexibility in certification. If the work is carried out in stages:
  the gasfitting could be certified as a single job under a single CoC and GSC; or
  each part installation could be certified separately under its own CoC and GSC, etc.
  How this is done will depend on how the project is managed, including the timing of each stage.
You could design a form that allows multiple entries, or use multiple forms so long as the requirements of the regulations are met.
Notes: The approach to this depends on how the work is organised and supervised.

## Slide 35: Clarification – date of connection
What is the reference to “date connected or date work completed if not disconnected” on the Energy Safety GSC form?
The term “date connected or date work completed if not disconnected” comes about because the GSC has to completed after connection to gas supply or (alternatively in cases where there is no re-connection to gas supply) after completion of the gasfitting work. Both scenarios are possible. - GSMR 52B(4).

## Slide 36: Information on CoCs
Why is information on test results not requested as part of the CoC – it provides a lot of information at the time of installation?
Regulations limit required information to that necessary to establish compliance
Other information can be provided or recorded elsewhere

## Slide 37: What is a Certified Design?
What is a Certified Design?
A Certified Design:
  Identifies the location of the installation
  Identifies the Standards (if any) with which the installation will comply
  Must be signed and dated by the person who completed the design
Certified Design provides a means for identifying safe alternatives designs to the means of compliance
Designs certified as compliant and safe by the designer may be relied on by installers acting in good faith

## Slide 38: When is a Certified Design required?
When is a Certified Design required?
Certified Design may be used at any time to provide guidance or instructions for gasfitting work
A Certified Design is required where a gas installation or part installation does not comply with the recognised means of compliance
  AS/NZS 5601.1 sections 3 to 6 or
  AS/NZS 5601.2 sections 3 to 9

## Slide 39: Monitoring
Regulators – Energy Safety, PGDB & EWRB have independent access to EGHR database
Regulators can use EGHR to plan their monitoring programmes
Gives ability to focus on areas of concern
Currently Energy Safety selecting High Risk records for analysis
  Feedback on how certificates are completed
  Too soon for trends to emerge

## Slide 40: EGHR – Records entered
March daily average – 144 high risk records
22 gas
122 electricity

## Slide 41: EGHR – User registrations
42 registrations in March
51% of gas practitioners registered
1300 users (41%) now registered

## Slide 42: Overview of changes I
Aligns Electricity (PEW) and Gas (gasfitting) certification regimes
  Extends certification to all gasfitting
  Reflects international certification architecture
  Adopts risk management principles
  Allows integration of certification with other business processes
  Fee for certificate is removed

## Slide 43: Overview of changes II
Implements risk-based regime
  Updating expected – to reflect changes in environment & state of knowledge
  Reflecting new technology
Clarifies roles and accountabilities for all parties involved in delivering safety
More explicit connections:
  Ability to rely on other ‘certification’:
      Certified Design & Manufacturer’s Instructions
      CoCs & GSCs
  Need to test & verify (‘be satisfied’)

## Slide 44: Overview of changes III
Creates a register of high risk work
Introduces ‘safe to use’ certification (GSC)
Provides clarity for owners and occupiers
Links to other legislation
  Consumer protection
  Building Act
Improves potential for auditing and enforcement

## Slide 45: IPI Systems I
Increased Pressure Installation (IPI)
Domestic installation system
Used mid 1987 to 1991
  About 4000 installations
‘High’ installation pressure
  35 kPa
Narrow bore nylon or copper tubing
  ≤ 8 mm OD
Separate line to each appliance
  Manifold downstream of meter
  Secondary regulator before appliance

## Slide 46: IPI Systems II
Approval withdrawn in 1991
Vulnerability to rodent damage identified
Existing systems accepted
  If complied with IPI Interim Specifications
Mixed installations acceptable
  IPI at 35 kPa off manifold
  Conventional at ≤ 7 kPa off tee before manifold

## Slide 47: IPI Systems III
Systems not accepted:
  Conventional > 7 kPa (domestic)
  Hybrid conventional > 7 kPa + IPI
  IPI tube branched after manifold
Bulletin (2003)
  Description of IPI systems
  Gives recommended checks for IPI systems
  Provides guidance on how to go about modifying non-complying installations
www.energysafety.govt.nz

## Slide 48: Energy Safety
www.worksafe.govt.nz
www.energysafety.govt.nz
8 April 2014