QUESTIONS ARISING BY MR GORDON Q. Just to continue on from that, so in the case of Mr Gee with the bayonets where Mr Gee says he put the bayonets - there is a possibility if he had of, hypothetically, had of connected up the fryers, as you said, the bayonets right height, the hose the right length, the chances are it wouldn't be on the ground and we wouldn't be sitting here would you agree with that? A. That's correct. Q. So a lot of that hinges on whether that installation was altered from the time Mr Gee had finished the job and signed off on it - A. Well unfortunately it hinges on the height, the length and the position of the permanent connection. Q. So the main thing in that is the height? A. The height, the length and the permanent connection. Q. That's fine. Now, the second thing I have just to clarify and you're talking about Part 1 and Part 2 of the Act. Now Part 1 is what must be done, what you must comply with? A. Part 1 is the mandatory requirement. Q. Mandatory requirement, yes, and Part 2 is a way of compliance? A. That's correct.________________________________________________________________________ 433 

Q. Now, the reason I was asking about that, because on page 35 of the edition I have here, 1.5.7, it meanings about flue terminals and in the second paragraph of that section it reads: "Flue terminals shall be located to minimise entry of combustion products into any building and to minimise the effects of adverse draft on the performance of the gas appliances". So in reading that, if there's no gas entering into a building, then it complies with Part 1? A. Yes, the aim of that is to make sure that gas does not enter into the building. Q. So that's the aim of it, so if there is no gas, say in this case we've got two situations where people are saying there's no gas entering, then according to that paragraph then it complies with Part 1 of the Act? A. No, I don't rely on consumers whether the gas was entering or not, it is the gas fitter's job to locate it in such a way that gas does not enter the building. Q. But that's what it's saying here though isn't it, it's saying that if the flues aren't entering the building then it complies with Part 1? A. Yes, but - Q. And if the customers are saying fumes aren't entering the building then it's compliant with Part 1? A. But in order to ensure that under all conditions products of combustion do not enter into the premises, then one way of complying is to ensure that the clearances are in accordance with Part 2. If you are putting in an appliance with clearances other than those in Part 2, then you need to demonstrate how the - how you have ensured that under all conditions the products of combustion can't enter the property. Q. That doesn't say "in all conditions" there. Does it say in here "all conditions"? A. No it doesn't say all conditions, but that's surely a general inference from the requirements of the standard to meet all conditions. 

Q. Well an inference is fine, but as per it says here the - that's located to minimise entry of combustion products and to minimise the effects of adverse draft et cetera. So those - if there's no fumes entering those two ________________________________________________________________________ 434 

locations that we've been talking about, then they're actually compliant with the mandatory part of the NSZ 5261? A. I don't have any knowledge of whether products of combustion are in fact entering or not. I have not carried out any tests to demonstrate. I am unaware of any tests that have been carried out to demonstrate that. MR PARKER: Well I think we have reached the point where we are having submissions, so I think we can adjourn now. MR BICKERS Q. Mr Hammond, I'm sorry I'm just thinking about what Mr Gordon had put, under what circumstances does 1.5.7 take precedence over 1.6.2? And 1.6.2 which is the manufacturer's instructions, which in turn is table 16, so what would be necessary to say that you've complied with 1.5.7 and you can override 1.6.2? A. If the manufacturer had carried out some tests and designed a particular appliance in a particular fashion that he felt that it could be put closer to some other part of the building or whatever, then presumably he would provide that information to the gasfitters so they could see that it was appropriate to do so other than was specified in the means of complying. MS INESON Q. Supplementary on that, so does that mean on page 101, is that the point of number 6? A. Sorry? Q. In page 101 is that the point of note 6 at the bottom of the page? A. Yes, that note is there specifically for. Q. To describe what you've just described? A. Yeah. (Witness excused)________________________________________________________________________ 435 

MR PARKER: I think we'll adjourn and I thank you all. We will receive your written submissions on the agreed timetable, the 10th and the 16th. ADJOURNED [3.39 PM]
Best Regards Paul Gee
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